# UNIVERSITY OF MINING AND GEOLOGY “Engineering” LTD Laboratory "Lighting" www.light-bg.eu tel. (02) 8060 302, e-mail: candela@mail.bg

Measurement report number 2017-030/27.01.2017

testing samples of products

Model number or type, referring to the manufacturer: LED luminaire EMILI 48

Company identification: “Security Smart Systems “Ltd.

Applicant testing:  “Security Smart Systems “Ltd. 6 Gourko str. Vratza

Type of test: control measurements

Metrological traceability:

- LMT Photometer B520, ID 04B4021 with photometric head P30SC0 ID 04B4022, calibration certificate of the LMT Lichtmesstechnik GMBH Berlin №04B402/28.05.2014;

- luxmeter PU 550, ID 263621/2586, calibration certificate of the METRA BLANSKO a.s.№2887/2012, 19.12.2012;

- luxmeter KYORITSU 5202, ID K0017929, calibration certificate of the National Centre of Metrology 181-ОИ/15.12.2012;

- luminance-meter L 1003 of angular field 1o, producer “LMT” Germany, ID 0686191, calibration certificate of the National Centre of Metrology №182-ОИ/15.12.2012;

- Ulbricht photometer with diameter 2м;

- Automated goniophotometer.

- Power Meter  HM8115-2 ID 015447345, calibration certificate of the National Centre of Metrology 148-EEИ/14.12.2012;

- Digital thermometer with temperature sensor DS18B20 ID 0000011697CDH, calibration certificate of the National Centre of Metrology 268-TИ/14.11.2012;

- Ampermeter  Д5101 ID 737/1990, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №733/21.11.2012;

- MEGER  UT512 ID 1111074682, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №732/21.11.2012;

- Laser rangefinder DLE-40

- spectroradiometer МК350 ID HS0313220158, test source МК002, calibration certificate of UPRtek lab № А012001 / 2013/7/5

Technical specifications of documentation:  LED luminaire EMILI 48

Luminaire

| TEST REPORT 2017-030-27.01.2017 | page 1 | all pages 4 |
| --- | --- | --- |

| TEST REPORT 2017-030-27.01.2017 | page 2 | all pages 4 |
| --- | --- | --- |

Results of test

| Operating voltage | AC 230 V | Spectrum of light Kpuls.= 8.4 % |
| --- | --- | --- |
| Operating Current | AC 0.226 A |  |
| Wattage including ballast (watts) | 50.8 W |  |
| Power factor | 0.97 |  |
| color temperature | 4070 K |  |
| Color rendering index CRI | 82 |  |
| color coordinates CIE 1931 | x=0.3779, y=0.3767 |  |
| color coordinates CIE 1976 | u’=0.2234, v’=0.5012 |  |
| Luminous flux emitted by a luminaire | 5787 lm |  |
| Light output of the luminaire | 114lm /W |  |

Luminaire light distribution of polar coordinates in the conditional flux 1000lm

Luminaire light distribution of the 3D

| TEST REPORT 2017-030-27.01.2017 | page 3 | all pages 4 |
| --- | --- | --- |

Light distribution of luminaries are in tabular form

for conditional luminous flux 1000lm:

gm/C     0   15   30   45   60   75   90  105  120  135  150  165  180

0.0  402  402  402  402  401  401  399  401  401  402  402  402  402

2.5  401  400  399  399  399  399  400  399  399  399  399  400  401

5.0  400  402  402  402  401  400  399  400  401  402  402  402  400

7.5  395  395  395  395  393  393  394  393  393  395  395  395  395

10.0  393  392  391  391  392  392  392  392  392  391  391  392  393

12.5  376  375  375  376  378  379  378  379  378  376  375  375  376

15.0  375  375  377  378  379  379  377  379  379  378  377  375  375

17.5  362  362  362  363  364  365  367  365  364  363  362  362  362

20.0  357  356  356  357  358  359  361  359  358  357  356  356  357

22.5  345  345  345  345  346  347  348  347  346  345  345  345  345

25.0  336  335  336  337  338  340  340  340  338  337  336  335  336

27.5  322  321  320  320  320  323  326  323  320  320  320  321  322

30.0  306  306  307  308  311  313  315  313  311  308  307  306  306

32.5  297  296  297  298  299  301  301  301  299  298  297  296  297

35.0  281  280  281  282  284  286  288  286  284  282  281  280  281

37.5  267  266  266  267  271  274  275  274  271  267  266  266  267

40.0  251  251  251  252  255  258  260  258  255  252  251  251  251

42.5  235  234  234  236  238  240  242  240  238  236  234  234  235

45.0  221  222  223  224  226  228  229  228  226  224  223  222  221

47.5  206  206  207  208  211  213  215  213  211  208  207  206  206

50.0  146  195  196  197  199  202  203  202  199  197  196  195  146

52.5  183  183  184  186  188  191  192  191  188  186  184  183  183

55.0  172  173  173  175  177  179  181  179  177  175  173  173  172

57.5  159  158  159  161  163  165  166  165  163  161  159  158  159

60.0  142  142  143  144  146  147  149  147  146  144  143  142  142

62.5  126  127  127  129  130  132  134  132  130  129  127  127  126

65.0  114  114  114  115  117  118  119  118  117  115  114  114  114

67.5   98   98   99  100  101  102  103  102  101  100   99   98   98

70.0   85   85   86   87   88   90   91   90   88   87   86   85   85

72.5   74   74   75   76   76   78   79   78   76   76   75   74   74

75.0   57   57   58   58   59   60   60   60   59   58   58   57   57

77.5   45   45   46   46   46   47   47   47   46   46   46   45   45

80.0   35   36   36   36   37   37   37   37   37   36   36   36   35

82.5   25   25   26   26   26   26   26   26   26   26   26   25   25

85.0   16   16   17   17   17   17   17   17   17   17   17   16   16

87.5    7    8    8    8    8    8    8    8    8    8    8    8    7

90.0    2    2    3    3    2    2    5    2    2    3    3    2    2

92.5    2    2    2    2    2    1    1    1    2    2    2    2    2

95.0    2    2    2    2    2    1    1    1    2    2    2    2    2

Changing the light flux

| TEST REPORT 2017-030-27.01.2017 | page 4 | all pages 4 |
| --- | --- | --- |

Distribution of illumination in height hanging lamp 5 м

Coordinates of the luminaire X=15m, Y=5m.

Applications:

Files with the EULUMDAT format. Light distribution is captured in γ-С planes with step 2.5о in plane γ (от 0 о - 95 о) и 5о in plane С (от 0 о - 360 о) accordance with EN 13032-1 p 4.2.3.

Files with the measured values

- 2017-030.ldt

(photometric data in a standard format),

Test results relate only to test samples.

Sofia 27.01.2017

Manager of Laboratory "Lighting":

- /assoc. prof. d-r. Krasimir Velinov/

Manager:

/ prof. d-r. L. Totev/