# UNIVERSITY OF MINING AND GEOLOGY “Engineering” LTD Laboratory "Lighting" www.light-bg.eu tel. (02) 8060 302, e-mail: candela@mail.bg

Measurement report number 2017-069/20.02.2017

testing samples of products

Model number or type, referring to the manufacturer: LUPO

Company identification: “ISS” Ltd. 6, Gurko street,  Vratsa, Bulgaria

Applicant testing: “ISS” Ltd. 6, Gurko street,  Vratsa, Bulgaria

Type of test: control measurements

Metrological traceability:

- LMT Photometer B520, ID 04B4021 with photometric head P30SC0 ID 04B4022, calibration certificate of the LMT Lichtmesstechnik GMBH Berlin №04B402/28.05.2014;

- luxmeter PU 550, ID 263621/2586, calibration certificate of the METRA BLANSKO a.s.№2887/2012, 19.12.2012;

- luxmeter KYORITSU 5202, ID K0017929, calibration certificate of the National Centre of Metrology 181-ОИ/15.12.2012;

- luminance-meter L 1003 of angular field 1o, producer “LMT” Germany, ID 0686191, calibration certificate of the National Centre of Metrology 130-ОИ/20.12.2010;

- Ulbricht photometer with diameter 2м;

- Automated goniophotometer.

- Power Meter  HM8115-2 ID 015447345, calibration certificate of the National Centre of Metrology 148-EEИ/14.12.2012;

- Digital thermometer with temperature sensor DS18B20 ID 0000011697CDH, calibration certificate of the National Centre of Metrology 268-TИ/14.11.2012;

- Ampermeter  Д5101 ID 737/1990, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №733/21.11.2012;

- MEGER  UT512 ID 1111074682, calibration certificate of ‘ЛК УНИСИСТ’ Ltd №732/21.11.2012;

- Laser rangefinder DLE-40

- spectroradiometer МК350 ID HS0313220158, test source МК002, calibration certificate of UPRtek lab № А012001 / 2013/7/5

Technical specifications of documentation:

LED Luminaire LUPO – 2 pcs

Luminaire

| TEST REPORT 2017-069-20.02.2017 | page 1 | all pages 4 |
| --- | --- | --- |

| TEST REPORT 2017-069-20.02.2017 | page 2 | all pages 4 |
| --- | --- | --- |

Results of the test of luminarie – Var  1 & 2

| Operating voltage | AC 230 V | Spectrum of light Koef. puls.= 41.7% |
| --- | --- | --- |
| Operating Current | AC 0.144 A |  |
| Wattage including ballast (watts) | 30,52 W |  |
| Power factor | 0.94 |  |
| color temperature | 4086 K |  |
| Color rendering index CRI | 80 |  |
| color coordinates CIE 1931 | x=0.3773, y=0.3768 |  |
| color coordinates CIE 1976 | u’=0.2230, v’=0.5011 |  |
| Luminous flux emitted by a luminaire | 4308 lm |  |
| Light output of the luminaire | 141,3 lm /W |  |
| Luminous flux emitted by a luminaire Var2 | 4283 lm |  |
| Light output of the luminaire Var2 | 140,9 lm /W |  |

Luminaire light distribution of polar coordinates in the conditional flux 1000lm

Luminaire light distribution of the 3D

| TEST REPORT 2017-069-20.02.2017 | page 3 | all pages 4 |
| --- | --- | --- |

Light distribution of luminaries are in tabular form

for conditional luminous flux 1000lm:

gm/C   0   15   30   45   60   75   90  105  120  135  150  165  180

0.0  397  398  397  397  398  398  398  398  398  397  397  398  397

2.5  392  392  394  394  393  394  395  394  393  394  394  392  392

5.0  392  393  394  395  394  397  398  397  394  395  394  393  392

7.5  385  387  386  389  389  390  391  390  389  389  386  387  385

10.0  379  382  385  389  390  390  391  390  390  389  385  382  379

12.5  373  375  376  377  379  380  381  380  379  377  376  375  373

15.0  373  374  375  377  378  380  381  380  378  377  375  374  373

17.5  358  360  360  362  364  367  369  367  364  362  360  360  358

20.0  357  359  361  363  365  366  367  366  365  363  361  359  357

22.5  340  343  344  346  349  352  354  352  349  346  344  343  340

25.0  334  337  339  340  344  345  347  345  344  340  339  337  334

27.5  316  317  320  324  328  330  332  330  328  324  320  317  316

30.0  309  310  312  315  317  319  321  319  317  315  312  310  309

32.5  298  299  302  305  307  310  312  310  307  305  302  299  298

35.0  282  284  286  289  291  294  296  294  291  289  286  284  282

37.5  266  269  271  275  277  280  281  280  277  275  271  269  266

40.0  252  254  256  259  260  263  266  263  260  259  256  254  252

42.5  235  237  239  242  244  247  249  247  244  242  239  237  235

45.0  220  222  224  227  229  232  233  232  229  227  224  222  220

47.5  205  207  208  211  213  215  218  215  213  211  208  207  205

50.0  194  194  197  199  201  204  206  204  201  199  197  194  194

52.5  180  182  185  187  189  192  193  192  189  187  185  182  180

55.0  167  168  170  173  175  178  179  178  175  173  170  168  167

57.5  156  157  160  162  165  167  169  167  165  162  160  157  156

60.0  138  140  143  145  148  150  152  150  148  145  143  140  138

62.5  124  125  128  130  132  135  137  135  132  130  128  125  124

65.0  109  111  113  115  118  120  122  120  118  115  113  111  109

67.5   93   95   97   99  101  104  106  104  101   99   97   95   93

70.0   81   82   84   86   88   90   93   90   88   86   84   82   81

72.5   70   71   72   74   76   78   80   78   76   74   72   71   70

75.0   52   53   54   56   58   60   62   60   58   56   54   53   52

77.5   40   41   42   43   45   47   48   47   45   43   42   41   40

80.0   30   31   32   33   35   36   38   36   35   33   32   31   30

82.5   19   20   20   22   23   24   26   24   23   22   20   20   19

85.0   10   11   11   12   13   15   16   15   13   12   11   11   10

87.5    2    3    3    4    5    6    7    6    5    4    3    3    2

90.0    1    1    1    1    3    3    4    3    3    1    1    1    1

92.5    1    1    1    1    1    1    1    1    1    1    1    1    1

95.0    1    1    1    1    1    1    1    1    1    1    1    1    1

Changing the light flux

| TEST REPORT 2017-069-20.02.2017 | page 4 | all pages4 |
| --- | --- | --- |

Distribution of illumination in height hanging lamp 5m

Coordinates of the luminaire X=15m, Y=5m.

Applications:

Files with the EULUMDAT format. Light distribution is captured in γ-С planes with step 2.5о in plane γ (от 0 о - 95 о) и 5о in plane С (от 0 о - 360 о) accordance with EN 13032-1 p 4.2.3.

Files with the measured values

- 2017-069.ldt (Var-1 ),

- 2017-069-1.ldt (Var-2),

Test results relate only to test samples.

Sofia 20.02.2017

Manager of Laboratory "Lighting":

- /assoc. prof. d-r. Krasimir Velinov/

Manager:

/ prof. d-r. L. Totev/